# Technical Note: Architecting Mineral Insulated (MI) Cable Systems for High-Temperature EHT

# 1. Introduction & The Physics of MI Cables

Mineral Insulated (MI) cables are Series Resistance heaters, built with alloy conductors and magnesium oxide insulation to withstand temperatures up to 600°C (1112°F). Unlike self-regulating cables, they output a constant wattage based on Ohm's Law and cannot be cut in the field.

## Key Mathematical Formulas

1. Total Resistance (Ω): R_total = R_base × (L_pipe + L_allowances) × C_temp

Where C_temp is the temperature correction multiplier for the specific alloy (e.g., Alloy 825).

2. Power Output (Single Phase): P_total (W) = V² / R_total

3. Power Output (3-Phase Star/Wye): P_total (W) = (V_line / √3)² / R_total

4. Watt Density (W/m): W_density = P_total / L_pipe

5. Operating Current (A): I = P_total / V_applied

# 2. Engineering & Calculation Algorithm

Step 1: Calculate Heat Loss (Q_loss) based on insulation and pipe size.

Step 2: Select phase configuration (1-Phase loop, 3-Phase Star, Dual-Core).

Step 3: Iterate through available cable resistances (Ohms/km) using the formulas above.

Step 4: Filter cables where W_density < Q_loss.

Step 5: Sheath Temperature Validation. Calculate Maximum Sheath Temperature (MST) using standard IEC/IEEE heat transfer equations. If MST > T-Class Limit (e.g., 200°C), discard.

# 3. Subtle Aspects & Industry Practice

1. The As-Built Nightmare: If the pipe is built shorter than the isometric design, the factory-terminated cable must be serpentined. This increases the W/m density locally and can cause a catastrophic sheath temperature spike, violating hazardous area T-classes.

2. Star-Point Imbalance: In a 3-Phase Star configuration, if one phase runs around an extra valve, its resistance changes, shifting the neutral point and causing unbalanced heating.

# 4. Innovative Software Features

1. Dynamic As-Built Tolerance Simulator: Graphically showing how the MST shifts if the pipe is ±5% length.

2. 3-Phase Star Auto-Balancer: Automatically calculating cold lead adjustments to balance asymmetrical pipes.